## OutputA
Project Name: CNSW-SNW Option 2 (SNW South loop) | [5 empty] | Indirect Cost Selection
Project Description: A new 500 kV double-circuit line from Bannaby to locality of South Creek. A new 330 kV line from locality of South Creek to Sydney West substation. | [5 empty] | Total Network Elements Cost Category |  |  | Above $1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Bannaby to locality of South Creek overhead line | 412233729.3797 | 100428888.9496 | 91776244.7306 | 117731450.4952 | 0 | 16650971.7579 | 0 | 22646173.4463 | 13860000 | 49140000
2 | Bannaby Substation | 64762855.0818 | 16590623.3541 | 30757342.7438 | 4541076.945 | 3908117.2693 | 2980076.5608 | 1026330.3402 | 4824887.8686 | 17400 | 117000
3 | Near South Creek substation | 195162941.5227 | 74864942.5853 | 71384035.7534 | 15043502.1532 | 10352379.5649 | 8875907.3865 | 2893255.9658 | 11373918.1137 | 82500 | 292500
4 | Near South Creek to Sydney West | 22131945.5979 | 5258262.5943 | 5197070.0938 | 5182791.355 | 0 | 877471.4391 | 0 | 1390100.1157 | 929775 | 3296475
5 | Eraring-Kemps Creek 500 kV line diversion near South Creek | 6580554.774 | 1914626.154 | 1442692.5274 | 1974664.5005 | 0 | 284203.1109 | 0 | 301608.4813 | 73080 | 589680
6 | Bayswater-Sydney West and Regentville-Sydney West line cut-in near South Creek | 7176317.0283 | 2367074.256 | 2031744.7808 | 850220.3405 | 0 | 292260.3891 | 0 | 364727.2619 | 140070 | 1130220
7 | Sydney West substation | 12621418.2129 | 815055.4686 | 8051872.4394 | 758709.5117 | 1250537.1174 | 374434.2698 | 241178.1686 | 1096031.2375 | 4350 | 29250
8 | Bannaby to near South Creek underground cable | 1092531131.6344 | 460265354.1053 | 513199536 | 27022871.7948 | 0 | 8368171.2576 | 1648276.1568 | 82026922.32 | 0 | 0
9 | Transition station between OHL and UH | 57436720.3723 | 9846709.1566 | 28999075.7628 | 4316437.2042 | 4476221.2907 | 2914162.3661 | 1048228.8393 | 5667885.7528 | 21750 | 146250
| Total Network Element Cost | 1870637613.6042 | 672351536.6237 | 752839614.8319 | 177421724.3001 | 19987255.2423 | 41617658.5378 | 6857269.4707 | 129692254.5977 | 15128925 | 54741375
Indirect Costs
| Project Development | 41341091.26
| Works Delivery | 51068406.85
| Land and Environment | 9727315.59
| Stakeholder and Community Engagement | 12767101.71
| Procurement Costs | 6079572.24
| Insurance | 4863657.8
| Total Indirect Cost | 125847145.46
| Total Expected Project Cost | 1996484759.06
Post TCD calculation Including increased unknown risk allowance for Class 5b (with accuracy of +/-50%):
| Total Expected Project Cost Class 5b | 2256895814.5896
Note: Class 5b unknown risk allowance only applied on final cost shown on 'OutputA'. Has not been applied to individual cost components in 'OutputB' and 'OutputC'
Please see Transmission Cost Report for details on Class 5a and 5b risk allowances and accuracy.

## OutputB
Project Name: CNSW-SNW Option 2 (SNW South loop) |  |  |  |  | Indirect Cost Selection
Project Description: A new 500 kV double-circuit line from Bannaby to locality of South Creek. A new 330 kV line from locality of South Creek to Sydney West substation. |  |  |  |  | Total Network Elements Cost Category |  |  | Above $1500 million
[5 empty] | Greenfield or Brownfield |  |  | Brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1215681552.8533 | 471655515.724 | 470724898.4048 | 108123463.856 | 13747970 | 27368798.4643 | 4536908 | 86772748.4043 | 4678750 | 28072500
Adjusted Baseline Cost | 1469507165.229 | 526798691.2749 | 593387329.9499 | 140850012.5462 | 16790622.0672 | 34057984.6415 | 5588728.5826 | 114770796.1666 | 9190500 | 28072500
Known Risk Allowance | 155468614.9944 | 55957289.8604 | 58894391.7708 | 11826443.6381 | 510133.6443 | 1749516.7383 | 361262.758 | 10330626.5844 | 1802700 | 14036250
Unknown Risk Allowance | 245661833.3808 | 89595555.4883 | 100557893.1111 | 24745268.1158 | 2686499.5308 | 5810157.1581 | 907278.13 | 4590831.8467 | 4135725 | 12632625
Total Network Element Cost | 1870637613.6042 | 672351536.6237 | 752839614.8319 | 177421724.3001 | 19987255.2423 | 41617658.5378 | 6857269.4707 | 129692254.5977 | 15128925 | 54741375
Indirect Costs:
Project Development | 41341091.2607
Works Delivery | 51068406.8514
Land and Environment | 9727315.5907
Stakeholder and Community Engagement | 12767101.7128
Procurement Costs | 6079572.2442
Insurance | 4863657.7954
Total Indirect Cost | 125847145.4552
Total Expected Project Cost | 1996484759.0594

## OutputC
Project Name: CNSW-SNW Option 2 (SNW South loop)
Project Description: A new 500 kV double-circuit line from Bannaby to locality of South Creek. A new 330 kV line from locality of South Creek to Sydney West substation.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | Bannaby to locality of South Creek overhead line | 500 kV line double circuit line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6080MVA | 500 | 100 | km | 74226075 | 54726787.5048 | 70204050 | 0 | 10778645.7143 | 0 | 14856215.7143 | 4200000 | 25200000 | 254191773.9333 | 61.66%
TRUE | TRUE | Baseline Cost | [6 empty] | 74226075 | 54726787.5048 | 70204050 | 0 | 10778645.7143 | 0 | 14856215.7143 | 4200000 | 25200000 | 254191773.9333 | 61.66%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Partly brownfield | - | - | - | 0 | 0.06 | 0.06 | 0 | 0.06 | 0.06 | 0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 10 to 100 km | - | - | - | 0.0336 | 0.055944 | 0.055944 | 0 | 0.055944 | 0.055944 | 0.0672 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.1036 | 0.33094 | 0.33094 | 0 | 0.25594 | 0.25594 | 0.3472 | 1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 81915896.37 | 72838289.4687 | 93437659.1232 | 0 | 13537375.413 | 0 | 20014293.8103 | 8400000 | 25200000 | 315343514.1852 | 76.5%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.08 | 0.08 | 0 | 0.05 | 0.05 | 0.0915 | 0.2 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 3768131.233 | 5827063.1575 | 7475012.7299 | 0 | 676868.7706 | 0 | 1831307.8836 | 1680000 | 12600000 | 33858383.7747 | 8.213%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 85684027.603 | 78665352.6262 | 100912671.8531 | 0 | 14214244.1836 | 0 | 21845601.6939 | 10080000 | 37800000 | 349201897.9598 | 84.71%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 14744861.3466 | 13110892.1044 | 16818778.6422 | 0 | 2436727.5743 | 0 | 800571.7524 | 3780000 | 11340000 | 63031831.4199 | 15.29%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 100428888.9496 | 91776244.7306 | 117731450.4952 | 0 | 16650971.7579 | 0 | 22646173.4463 | 13860000 | 49140000 | 412233729.3797 | 100%
Network Element 2
|  | Bannaby Substation | 500 kV Extension
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | (blank) | 1 | lot | 310068 | 10852380 | 775170 | 1705374 | 310068 | 310068 | 1240272 | 10000 | 60000 | 15573400 | 24.05%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 1CB | 500 | 2 | lot | 1614000 | 2270100 | 444000 | 200000 | 452810 | 90562 | 559673.16 | 0 | 0 | 5631145.16 | 8.695%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 1624000 | 1347600 | 429000 | 200000 | 360060 | 72012 | 445034.16 | 0 | 0 | 4477706.16 | 6.914%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 6978000 | 3000000 | 550000 | 200000 | 236000 | 80000 | 0 | 0 | 0 | 11044000 | 17.05%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 3094000 | 2620200 | 768000 | 400000 | 688220 | 137644 | 850639.92 | 0 | 0 | 8558703.92 | 13.22%
TRUE | TRUE | Baseline Cost | [6 empty] | 13620068 | 20090280 | 2966170 | 2705374 | 2047158 | 690286 | 3095619.24 | 10000 | 60000 | 45284955.24 | 69.92%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.24468 | 0.24468 | 0.23468 | 0.2442 | 0.2442 | 0.426 | 0.2 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 14277644.883 | 25005969.7104 | 3691932.4756 | 3340271.1703 | 2547073.9836 | 858853.8412 | 4414353.0362 | 12000 | 60000 | 54208099.1004 | 83.7%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.07 | 0.07 | 0.01 | 0.01 | 0.035 | 0.053 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 28555.2898 | 1750417.8797 | 258435.2733 | 33402.7117 | 25470.7398 | 30059.8844 | 233960.7109 | 0 | 30000 | 2390302.4897 | 3.691%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 14306200.1728 | 26756387.5901 | 3950367.7489 | 3373673.882 | 2572544.7234 | 888913.7256 | 4648313.7472 | 12000 | 90000 | 56598401.5901 | 87.39%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2284423.1813 | 4000955.1537 | 590709.1961 | 534443.3873 | 407531.8374 | 137416.6146 | 176574.1214 | 5400 | 27000 | 8164453.4917 | 12.61%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 16590623.3541 | 30757342.7438 | 4541076.945 | 3908117.2693 | 2980076.5608 | 1026330.3402 | 4824887.8686 | 17400 | 117000 | 64762855.0818 | 100%
Network Element 3
|  | Near South Creek substation | 500/330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 4 | lot | 9208000 | 5940600 | 2184000 | 1200000 | 1853260 | 370652 | 2290629.36 | 0 | 0 | 23047141.36 | 11.81%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 1624000 | 1347600 | 429000 | 200000 | 360060 | 72012 | 445034.16 | 0 | 0 | 4477706.16 | 2.294%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 2 | ea. | 36676000 | 6000000 | 3374000 | 200000 | 1688000 | 422000 | 0 | 0 | 0 | 48360000 | 24.78%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 6978000 | 3000000 | 550000 | 200000 | 236000 | 80000 | 0 | 0 | 0 | 11044000 | 5.659%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 3 | lot | 4584000 | 2799300 | 1097100 | 900000 | 938040 | 187608 | 1159417.44 | 0 | 0 | 11665465.44 | 5.977%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1038000 | 824150 | 261300 | 200000 | 232345 | 46469 | 287178.42 | 0 | 0 | 2889442.42 | 1.481%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | (blank) | 2 | lot | 758670 | 26553450 | 1896675 | 4172685 | 758670 | 758670 | 3034680 | 25000 | 150000 | 38108500 | 19.53%
TRUE | TRUE | Baseline Cost | [6 empty] | 60866670 | 46465100 | 9792075 | 7072685 | 6066375 | 1937411 | 7216939.38 | 25000 | 150000 | 139592255.38 | 71.53%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 62283646.0776 | 56207902.168 | 11845277.286 | 8555685.5908 | 7335460.65 | 2342717.3812 | 10038762.6776 | 50000 | 150000 | 158809451.8312 | 81.37%
FALSE | FALSE | Known Risks: | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.11 | 0.11 | 0.05 | 0.05 | 0.075 | 0.093 | 0.2 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2615913.1353 | 6182869.2385 | 1302980.5015 | 427784.2795 | 366773.0325 | 175703.8036 | 933604.929 | 10000 | 75000 | 12090628.9198 | 6.195%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 64899559.2129 | 62390771.4065 | 13148257.7875 | 8983469.8703 | 7702233.6825 | 2518421.1848 | 10972367.6066 | 60000 | 225000 | 170900080.751 | 87.57%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 9965383.3724 | 8993264.3469 | 1895244.3658 | 1368909.6945 | 1173673.704 | 374834.781 | 401550.5071 | 22500 | 67500 | 24262860.7717 | 12.43%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 74864942.5853 | 71384035.7534 | 15043502.1532 | 10352379.5649 | 8875907.3865 | 2893255.9658 | 11373918.1137 | 82500 | 292500 | 195162941.5227 | 100%
Network Element 4
|  | Near South Creek to Sydney West | 330 kV DCT
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 3 × Mango DCST 2400MVA | 330 | 7 | km | 3762904.08 | 2721302.5 | 2766624 | 0 | 515887.87 | 0 | 820177.87 | 281750 | 1690500 | 12559146.32 | 56.75%
TRUE | TRUE | Baseline Cost | [6 empty] | 3762904.08 | 2721302.5 | 2766624 | 0 | 515887.87 | 0 | 820177.87 | 281750 | 1690500 | 12559146.32 | 56.75%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 5 to 10 km | - | - | - | 0.0948 | 0.15784 | 0.15784 | 0 | 0.15784 | 0.15784 | 0.1896 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.1398 | 0.45784 | 0.45784 | 0 | 0.38284 | 0.38284 | 0.4946 | 1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4288958.0704 | 3967229.0792 | 4033300.6654 | 0 | 713391.4139 | 0 | 1225837.8445 | 563500 | 1690500 | 16482717.0734 | 74.47%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.13 | 0.105 | 0 | 0.05 | 0.075 | 0.094 | 0.2 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 197292.0712 | 515739.7803 | 423496.5699 | 0 | 35669.5707 | 0 | 115228.7574 | 112700 | 845250 | 2245376.7495 | 10.15%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4486250.1416 | 4482968.8595 | 4456797.2353 | 0 | 749060.9846 | 0 | 1341066.6019 | 676200 | 2535750 | 18728093.8229 | 84.62%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 772012.4527 | 714101.2343 | 725994.1198 | 0 | 128410.4545 | 0 | 49033.5138 | 253575 | 760725 | 3403851.775 | 15.38%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 5258262.5943 | 5197070.0938 | 5182791.355 | 0 | 877471.4391 | 0 | 1390100.1157 | 929775 | 3296475 | 22131945.5979 | 100%
Network Element 5
|  | Eraring-Kemps Creek 500 kV line diversion near South Creek | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 6 (4 × conductor/phase DCST) | 500 | 2 | lot | 1569365.7 | 1014266.4 | 1416139.2 | 0 | 207994.08 | 0 | 248769.78 | 50400 | 302400 | 4809335.16 | 73.08%
TRUE | TRUE | Baseline Cost | [6 empty] | 1569365.7 | 1014266.4 | 1416139.2 | 0 | 207994.08 | 0 | 248769.78 | 50400 | 302400 | 4809335.16 | 73.08%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1569365.7 | 1135978.368 | 1586075.904 | 0 | 232953.3696 | 0 | 278622.1536 | 50400 | 302400 | 5155795.4952 | 78.35%
FALSE | FALSE | Known Risks: | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.04 | 0.09 | 0.065 | 0 | 0.04 | 0.065 | 0.0425 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 62774.628 | 102238.0531 | 103094.9338 | 0 | 9318.1348 | 0 | 11841.4415 | 0 | 151200 | 440467.1912 | 6.693%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1632140.328 | 1238216.4211 | 1689170.8378 | 0 | 242271.5044 | 0 | 290463.5951 | 50400 | 453600 | 5596262.6864 | 85.04%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 282485.826 | 204476.1062 | 285493.6627 | 0 | 41931.6065 | 0 | 11144.8861 | 22680 | 136080 | 984292.0876 | 14.96%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 1914626.154 | 1442692.5274 | 1974664.5005 | 0 | 284203.1109 | 0 | 301608.4813 | 73080 | 589680 | 6580554.774 | 100%
Network Element 6
|  | Bayswater-Sydney West and Regentville-Sydney West line cut-in near South Creek | [6 empty] | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 5 (2 × conductor/phase SCST) | 330 | 4 | lot | 1940224.8 | 1428392 | 609739.2 | 0 | 213890.8 | 0 | 300830.8 | 96600 | 579600 | 5169277.6 | 72.03%
TRUE | TRUE | Baseline Cost | [6 empty] | 1940224.8 | 1428392 | 609739.2 | 0 | 213890.8 | 0 | 300830.8 | 96600 | 579600 | 5169277.6 | 72.03%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1940224.8 | 1599799.04 | 682907.904 | 0 | 239557.696 | 0 | 336930.496 | 96600 | 579600 | 5475619.936 | 76.3%
FALSE | FALSE | Known Risks: | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.04 | 0.09 | 0.065 | 0 | 0.04 | 0.065 | 0.0425 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 77608.992 | 143981.9136 | 44389.0138 | 0 | 9582.3078 | 0 | 14319.5461 | 0 | 289800 | 579681.7733 | 8.078%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2017833.792 | 1743780.9536 | 727296.9178 | 0 | 249140.0038 | 0 | 351250.0421 | 96600 | 869400 | 6055301.7093 | 84.38%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 349240.464 | 287963.8272 | 122923.4227 | 0 | 43120.3853 | 0 | 13477.2198 | 43470 | 260820 | 1121015.319 | 15.62%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2367074.256 | 2031744.7808 | 850220.3405 | 0 | 292260.3891 | 0 | 364727.2619 | 140070 | 1130220 | 7176317.0283 | 100%
Network Element 7
|  | Sydney West substation | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | (blank) | 1 | lot | 142467 | 4986345 | 356167.5 | 783568.5 | 142467 | 142467 | 569868 | 2500 | 15000 | 7140850 | 56.58%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 1 | lot | 543000 | 425200 | 153750 | 100000 | 122195 | 24439 | 151033.02 | 0 | 0 | 1519617.02 | 12.04%
TRUE | TRUE | Baseline Cost | [6 empty] | 685467 | 5411545 | 509917.5 | 883568.5 | 264662 | 166906 | 720901.02 | 2500 | 15000 | 8660467.02 | 68.62%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.2 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 701424.6718 | 6546237.7556 | 616837.0014 | 1068835.1431 | 320029.2904 | 201822.7352 | 1002773.3188 | 3000 | 15000 | 10475959.9163 | 83%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.07 | 0.07 | 0.01 | 0.01 | 0.035 | 0.053 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 1402.8493 | 458236.6429 | 43178.5901 | 10688.3514 | 3200.2929 | 7063.7957 | 53146.9859 | 0 | 7500 | 584417.5083 | 4.63%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 702827.5211 | 7004474.3985 | 660015.5915 | 1079523.4945 | 323229.5833 | 208886.5309 | 1055920.3047 | 3000 | 22500 | 11060377.4246 | 87.63%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 112227.9475 | 1047398.0409 | 98693.9202 | 171013.6229 | 51204.6865 | 32291.6376 | 40110.9328 | 1350 | 6750 | 1561040.7883 | 12.37%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 815055.4686 | 8051872.4394 | 758709.5117 | 1250537.1174 | 374434.2698 | 241178.1686 | 1096031.2375 | 4350 | 29250 | 12621418.2129 | 100%
Network Element 8
|  | Bannaby to near South Creek underground cable |  | Two 8km tunnel installed cable. Each tunnel to have a set of cable with total capacity of 3000 MVA.
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Underground Cable | HVAC tunnel installed cable | 3000MVA - 3000mm2 per cct double circuit installed in a tunnel | 500 | 16 | km | 306907406.144 | 320000000 | 17050411.456 | 0 | 5280000 | 1040000 | 56000000 | 0 | 0 | 706277817.6 | 64.65%
TRUE | TRUE | Baseline Cost | [6 empty] | 306907406.144 | 320000000 | 17050411.456 | 0 | 5280000 | 1040000 | 56000000 | 0 | 0 | 706277817.6 | 64.65%
FALSE | FALSE | Adjustments: | Underground cable project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable project attribute | Delivery timetable | Tight | - | - | - | 0.05 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0
FALSE | FALSE |  | Underground cable project attribute | Greenfield or brownfield | Brownfield (high density urban/city infrastructure interface) | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable project attribute | Project network element size | 1 to 5 km | - | - | - | 0.0948 | 0.15784 | 0.15784 | 0 | 0.15784 | 0.15784 | 0.1896 | 0 | 0
FALSE | FALSE |  | Underground cable project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.1448 | 0.25784 | 0.25784 | 0 | 0.25784 | 0.25784 | 0.2906 | 0 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 351347598.5537 | 402509440 | 21446723.6466 | 0 | 6641405.76 | 1308155.68 | 72273600 | 0 | 0 | 855526923.6403 | 78.31%
FALSE | FALSE | Known Risks: | Underground cable known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Underground cable known risk | Cultural heritage | BAU |  |  |  | 0 | 0.015 | 0 | 0 | 0 | 0 | 0.00495 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Underground cable known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Market activity | Tight |  |  |  | 0.1 | 0.05 | 0.05 | 0 | 0.05 | 0.05 | 0.05 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Underground cable known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.14 | 0.105 | 0.09 | 0 | 0.09 | 0.09 | 0.09495 | 0.2 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 49188663.7975 | 42263491.2 | 1930205.1282 | 0 | 597726.5184 | 117734.0112 | 6862378.32 | 0 | 0 | 100960198.9753 | 9.241%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 400536262.3512 | 444772931.2 | 23376928.7748 | 0 | 7239132.2784 | 1425889.6912 | 79135978.32 | 0 | 0 | 956487122.6156 | 87.55%
FALSE | FALSE | Unknown Risks: | Underground cable unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Underground cable unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 0
FALSE | FALSE |  | Underground cable unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.13 | 0.13 | 0.13 | 0 | 0.13 | 0.13 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.17 | 0.17 | 0.17 | 0 | 0.17 | 0.17 | 0.04 | 0 | 0
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 59729091.7541 | 68426604.8 | 3645943.0199 | 0 | 1129038.9792 | 222386.4656 | 2890944 | 0 | 0 | 136044009.0188 | 12.45%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 460265354.1053 | 513199536 | 27022871.7948 | 0 | 8368171.2576 | 1648276.1568 | 82026922.32 | 0 | 0 | 1092531131.6344 | 100%
Network Element 9
|  | Transition station between OHL and UH | 500 kV transition station
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 4604000 | 2970300 | 1092000 | 600000 | 926630 | 185326 | 1145314.68 | 0 | 0 | 11523570.68 | 20.06%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | N/A | 1 | lot | 379335 | 13276725 | 948337.5 | 2086342.5 | 379335 | 379335 | 1517340 | 12500 | 75000 | 19054250 | 33.17%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 3094000 | 2620200 | 768000 | 400000 | 688220 | 137644 | 850639.92 | 0 | 0 | 8558703.92 | 14.9%
TRUE | TRUE | Baseline Cost | [6 empty] | 8077335 | 18867225 | 2808337.5 | 3086342.5 | 1994185 | 702305 | 3513294.6 | 12500 | 75000 | 39136524.6 | 68.14%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0491 | 0.2496 | 0.2496 | 0.2396 | 0.249 | 0.249 | 0.476 | 0.2 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 8473932.1485 | 23576484.36 | 3509298.54 | 3825830.163 | 2490737.065 | 877178.945 | 5185622.8296 | 15000 | 75000 | 48029084.0511 | 83.62%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.07 | 0.07 | 0.01 | 0.01 | 0.035 | 0.053 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 16947.8643 | 1650353.9052 | 245650.8978 | 38258.3016 | 24907.3707 | 30701.2631 | 274838.01 | 0 | 37500 | 2319157.6126 | 4.038%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 8490880.0128 | 25226838.2652 | 3754949.4378 | 3864088.4646 | 2515644.4357 | 907880.2081 | 5460460.8396 | 15000 | 112500 | 50348241.6637 | 87.66%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1355829.1438 | 3772237.4976 | 561487.7664 | 612132.8261 | 398517.9304 | 140348.6312 | 207424.9132 | 6750 | 33750 | 7088478.7086 | 12.34%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 9846709.1566 | 28999075.7628 | 4316437.2042 | 4476221.2907 | 2914162.3661 | 1048228.8393 | 5667885.7528 | 21750 | 146250 | 57436720.3723 | 100%