## OutputA
Project Name: S4 Yorke Peninsula Option 1 | [5 empty] | Indirect Cost Selection
Project Description: String first circuit of a 275 kV double circuit line from Blythe West into new Yorke Peninsula substation. Cut-in Blythe West into Brinkworth - Templers West. | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | OHL: 275 circuit | 245258155.5322 | 61333290.1597 | 77143648.1492 | 15998465.7637 | 0 | 11113015.1918 | 0 | 16873520.6428 | 11748969.375 | 51047246.25
2 | Substation 275/132 kV | 47639196.6155 | 17190371.4421 | 19008098 | 3267858.0954 | 3034613.5923 | 1788100.2148 | 724339.5654 | 2509565.7055 | 21750 | 94500
3 | Substation 275/132 kV | 24006801.1382 | 2643526.0877 | 13924045.8476 | 1519941.9379 | 2389885.6311 | 917564.095 | 454398.5055 | 2070251.5334 | 16312.5 | 70875
4 | OHL: 275 kV circuit | 19053122.4791 | 4941460.3208 | 5616016.7415 | 2016408.2994 | 0 | 740128.9973 | 0 | 1167576.8701 | 855318.75 | 3716212.5
5 | Switching Station 275 kV | 21026211.67 | 3199657.0708 | 11122292.1343 | 1431572.6583 | 2045546.6542 | 923682.4703 | 390030.7788 | 1855304.9033 | 10875 | 47250
| Total Network Element Cost | 356983487.4349 | 89308305.0812 | 126814100.8724 | 24234246.7547 | 7470045.8776 | 15482490.9692 | 1568768.8497 | 24476219.6551 | 12653225.625 | 54976083.75
Indirect Costs
| Project Development | 14110001.28
| Works Delivery | 5644000.51
| Land and Environment | 5996750.54
| Stakeholder and Community Engagement | 3880250.35
| Procurement Costs | 3527500.32
| Insurance | 2116500.19
| Total Indirect Cost | 35275003.2
| Total Expected Project Cost | 392258490.64
Post TCD calculation Including increased unknown risk allowance for Class 5b (with accuracy of +/-50%):
| Total Expected Project Cost Class 5b | 443422641.593
Note: Class 5b unknown risk allowance only applied on final cost shown on 'OutputA'. Has not been applied to individual cost components in 'OutputB' and 'OutputC'
Please see Transmission Cost Report for details on Class 5a and 5b risk allowances and accuracy.

## OutputB
Project Name: S4 Yorke Peninsula Option 1 |  |  |  |  | Indirect Cost Selection
Project Description: String first circuit of a 275 kV double circuit line from Blythe West into new Yorke Peninsula substation. Cut-in Blythe West into Brinkworth - Templers West. |  |  |  |  | Total Network Elements Cost Category |  |  | $100-$500 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 259758831.2909 | 70758825.6144 | 92385557.25 | 17639392.3 | 5620616.5 | 11507191.8582 | 1164313.5 | 19959909.2682 | 5817575 | 34905450
Adjusted Baseline Cost | 286571051.9821 | 75703238.7425 | 106049781.352 | 20204028.8272 | 6439694.722 | 13173784.6726 | 1352386.9394 | 23506869.2263 | 8726362.5 | 31414905
Known Risk Allowance | 12756710.2082 | 374930.0879 | 2428426.1588 | 499806.8017 | 0 | 0 | 0 | 29075.6598 | 0 | 9424471.5
Unknown Risk Allowance | 57655725.2446 | 13230136.2508 | 18335893.3616 | 3530411.1258 | 1030351.1555 | 2308706.2966 | 216381.9103 | 940274.7691 | 3926863.125 | 14136707.25
Total Network Element Cost | 356983487.4349 | 89308305.0812 | 126814100.8724 | 24234246.7547 | 7470045.8776 | 15482490.9692 | 1568768.8497 | 24476219.6551 | 12653225.625 | 54976083.75
Indirect Costs:
Project Development | 14110001.2803
Works Delivery | 5644000.5121
Land and Environment | 5996750.5441
Stakeholder and Community Engagement | 3880250.3521
Procurement Costs | 3527500.3201
Insurance | 2116500.192
Total Indirect Cost | 35275003.2007
Total Expected Project Cost | 392258490.6356

## OutputC
Project Name: S4 Yorke Peninsula Option 1
Project Description: String first circuit of a 275 kV double circuit line from Blythe West into new Yorke Peninsula substation. Cut-in Blythe West into Brinkworth - Templers West.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | OHL: 275 circuit | Double circuit tower strung on 1 side for new Yorke REZ substation.
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | Stage 1 development: 1 × Olive DCST 900MVA | 275 | 151.1 | km | 48331224.22 | 55925509.75 | 11598133.8 | 0 | 8261236.39 | 0 | 14211554.39 | 5401825 | 32410950 | 176140433.55 | 71.82%
TRUE | TRUE | Baseline Cost | [6 empty] | 48331224.22 | 55925509.75 | 11598133.8 | 0 | 8261236.39 | 0 | 14211554.39 | 5401825 | 32410950 | 176140433.55 | 71.82%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | SA | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0.14 | 0.5 | -0.1
TRUE | TRUE | Adjusted Baseline | [6 empty] | 51714409.9154 | 63755081.115 | 13221872.532 | 0 | 9417809.4846 | 0 | 16201172.0046 | 8102737.5 | 29169855 | 191582937.5516 | 78.11%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 310286.4595 | 1912652.4335 | 396656.176 | 0 | 0 | 0 | 24301.758 | 0 | 8750956.5 | 11394853.3269 | 4.646%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 52024696.3749 | 65667733.5485 | 13618528.708 | 0 | 9417809.4846 | 0 | 16225473.7626 | 8102737.5 | 37920811.5 | 202977790.8785 | 82.76%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 9308593.7848 | 11475914.6007 | 2379937.0558 | 0 | 1695205.7072 | 0 | 648046.8802 | 3646231.875 | 13126434.75 | 42280364.6536 | 17.24%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 61333290.1597 | 77143648.1492 | 15998465.7637 | 0 | 11113015.1918 | 0 | 16873520.6428 | 11748969.375 | 51047246.25 | 245258155.5322 | 100%
Network Element 2
|  | Substation 275/132 kV | Yorke Connection Point susbtation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 1 | lot | 962200 | 712510 | 241200 | 200000 | 211591 | 42318.2 | 261526.48 | 0 | 0 | 2631345.68 | 5.523%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 600MVA | 275/132 | 1 | ea. | 11220000 | 1500000 | 1032000 | 100000 | 516000 | 129000 | 0 | 0 | 0 | 14497000 | 30.43%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 275 | 2 | lot | 1013400 | 735010 | 277800 | 200000 | 222621 | 44524.2 | 275159.56 | 0 | 0 | 2768514.76 | 5.811%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 132 | 1 | lot | 288580 | 269030 | 92550 | 100000 | 75016 | 15003.2 | 92719.78 | 0 | 0 | 932898.98 | 1.958%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 310068 | 10852380 | 775170 | 1705374 | 310068 | 310068 | 1240272 | 10000 | 60000 | 15573400 | 32.69%
TRUE | TRUE | Baseline Cost | [6 empty] | 13794248 | 14068930 | 2418720 | 2305374 | 1335296 | 540913.6 | 1869677.82 | 10000 | 60000 | 36403159.42 | 76.41%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | SA | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07246 | 0.15476 | 0.15476 | 0.13476 | 0.1544 | 0.1544 | 0.29 | 0.5 | -0.1
TRUE | TRUE | Adjusted Baseline | [6 empty] | 14793779.2101 | 16246237.6068 | 2793041.1072 | 2616046.2002 | 1541465.7024 | 624430.6598 | 2411884.3878 | 15000 | 54000 | 41095884.8744 | 86.26%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 29587.5584 | 162462.3761 | 27930.4111 | 0 | 0 | 0 | 1205.9422 | 0 | 16200 | 237386.2878 | 0.4983%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 14823366.7685 | 16408699.9829 | 2820971.5183 | 2616046.2002 | 1541465.7024 | 624430.6598 | 2413090.33 | 15000 | 70200 | 41333271.1621 | 86.76%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2367004.6736 | 2599398.0171 | 446886.5772 | 418567.392 | 246634.5124 | 99908.9056 | 96475.3755 | 6750 | 24300 | 6305925.4534 | 13.24%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 17190371.4421 | 19008098 | 3267858.0954 | 3034613.5923 | 1788100.2148 | 724339.5654 | 2509565.7055 | 21750 | 94500 | 47639196.6155 | 100%
Network Element 3
|  | Substation 275/132 kV | Blythe West substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 2 | lot | 1924400 | 1425020 | 482400 | 400000 | 423182 | 84636.4 | 523052.96 | 0 | 0 | 5262691.36 | 21.92%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 15000 m2 footprint area and applicable control building | N/A | 1 | lot | 247501 | 8662535 | 618752.5 | 1361255.5 | 247501 | 247501 | 990004 | 7500 | 45000 | 12427550 | 51.77%
TRUE | TRUE | Baseline Cost | [6 empty] | 2171901 | 10087555 | 1101152.5 | 1761255.5 | 670683 | 332137.4 | 1513056.96 | 7500 | 45000 | 17690241.36 | 73.69%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | SA | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Partly brownfield | - | - | - | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04746 | 0.17976 | 0.17976 | 0.16976 | 0.1794 | 0.1794 | 0.315 | 0.5 | -0.1
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2274979.4215 | 11900893.8868 | 1299095.6734 | 2060246.2337 | 791003.5302 | 391722.8496 | 1989669.9024 | 11250 | 40500 | 20759361.4975 | 86.47%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 4549.9588 | 119008.9389 | 12990.9567 | 0 | 0 | 0 | 994.835 | 0 | 12150 | 149694.6894 | 0.6236%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2279529.3803 | 12019902.8257 | 1312086.6301 | 2060246.2337 | 791003.5302 | 391722.8496 | 1990664.7374 | 11250 | 52650 | 20909056.1869 | 87.1%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 363996.7074 | 1904143.0219 | 207855.3077 | 329639.3974 | 126560.5648 | 62675.6559 | 79586.7961 | 5062.5 | 18225 | 3097744.9513 | 12.9%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2643526.0877 | 13924045.8476 | 1519941.9379 | 2389885.6311 | 917564.095 | 454398.5055 | 2070251.5334 | 16312.5 | 70875 | 24006801.1382 | 100%
Network Element 4
|  | OHL: 275 kV circuit | Single circuit 275 kV circuit for line cut-in of Blythe West into Brinkworth-Templers West.
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 × Lemon SCST 536MVA | 275 | 11 | km | 3893918.3944 | 4071347.5 | 1461801 | 0 | 550199.9682 | 0 | 983379.9682 | 393250 | 2359500 | 13713396.8309 | 71.97%
TRUE | TRUE | Baseline Cost | [6 empty] | 3893918.3944 | 4071347.5 | 1461801 | 0 | 550199.9682 | 0 | 983379.9682 | 393250 | 2359500 | 13713396.8309 | 71.97%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | SA | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0.14 | 0.5 | -0.1
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4166492.682 | 4641336.15 | 1666453.14 | 0 | 627227.9638 | 0 | 1121053.1638 | 589875 | 2123550 | 14935988.0996 | 78.39%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 24998.9561 | 139240.0845 | 49993.5942 | 0 | 0 | 0 | 1681.5797 | 0 | 637065 | 852979.2145 | 4.477%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4191491.6381 | 4780576.2345 | 1716446.7342 | 0 | 627227.9638 | 0 | 1122734.7435 | 589875 | 2760615 | 15788967.3141 | 82.87%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 749968.6828 | 835440.507 | 299961.5652 | 0 | 112901.0335 | 0 | 44842.1266 | 265443.75 | 955597.5 | 3264155.165 | 17.13%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4941460.3208 | 5616016.7415 | 2016408.2994 | 0 | 740128.9973 | 0 | 1167576.8701 | 855318.75 | 3716212.5 | 19053122.4791 | 100%
Network Element 5
|  | Switching Station 275 kV | Cut-in switching station (Blythe West cuts into Brinkworth - Templers West)
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 1 | lot | 962200 | 712510 | 241200 | 200000 | 211591 | 42318.2 | 261526.48 | 0 | 0 | 2631345.68 | 12.51%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 275 | 1 | lot | 1413700 | 812515 | 339300 | 300000 | 286551.5 | 57310.3 | 354177.65 | 0 | 0 | 3563554.45 | 16.95%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 191634 | 6707190 | 479085 | 1053987 | 191634 | 191634 | 766536 | 5000 | 30000 | 9616700 | 45.74%
TRUE | TRUE | Baseline Cost | [6 empty] | 2567534 | 8232215 | 1059585 | 1553987 | 689776.5 | 291262.5 | 1382240.13 | 5000 | 30000 | 15811600.13 | 75.2%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | SA | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07246 | 0.15476 | 0.15476 | 0.13476 | 0.1544 | 0.1544 | 0.29 | 0.5 | -0.1
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2753577.5136 | 9506232.5934 | 1223566.3746 | 1763402.2881 | 796277.9916 | 336233.43 | 1783089.7677 | 7500 | 27000 | 18196879.9591 | 86.54%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 5507.155 | 95062.3259 | 12235.6637 | 0 | 0 | 0 | 891.5449 | 0 | 8100 | 121796.6896 | 0.5793%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2759084.6687 | 9601294.9193 | 1235802.0383 | 1763402.2881 | 796277.9916 | 336233.43 | 1783981.3126 | 7500 | 35100 | 18318676.6487 | 87.12%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 440572.4022 | 1520997.2149 | 195770.6199 | 282144.3661 | 127404.4787 | 53797.3488 | 71323.5907 | 3375 | 12150 | 2707535.0213 | 12.88%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 3199657.0708 | 11122292.1343 | 1431572.6583 | 2045546.6542 | 923682.4703 | 390030.7788 | 1855304.9033 | 10875 | 47250 | 21026211.67 | 100%